## CHECKLIST FOR RESIDENTIAL ELECTRICAL VEHICLE CHARGING STATIONS

All forms available at <website>

- Completed Building Permit Application

- Electrical Load Calculations (if required)

- Equipment Manufacturer’s Installation Instructions

For Electronic Submittals:

- PDF files of all required forms

- Submit files by email to: _______

REQUIREMENTS:

Equipment Output Power (Continuous Load):
( 240v: 40amp (NEMA 14-50)  ( 240v: 30amp (hardwired only)  ( 240v: 24amp (14-30, L6-30)  ( 240v: 16amp (6-20)

(120v 16amp (5-20)    ( 12amp (5-15)    ( Other:

Equipment overcurrent protection rating:

( 50amp ( 40amp ( 30amp ( 20 amp  ( 15 amp   ( Other:

Existing electrical service:

( 100amp  ( 125amp   (150amp  ( Other:

Branch circuit distance:

( <100 feet  ( >100 feet

Conductor size:

( #14 Cu   (#12 Cu   ( #10 Cu     ( #8 Cu     ( #6 Cu     ( Other:

| Size of EV Charger Circuit Breaker | Required minimum size of conductors (THHN wire) | Conduit Type and Size* |
| --- | --- | --- |
|  |  | Electrical Metallic Tubing (EMT) | Rigid Nonmetallic Conduit – Schedule 40 (RNC) | Flexible Metal Conduit (FMC) |
| 20 amp | #12 | 1/2 “ | 1/2 “ | 1/2 “ |
| 30 amp | #12 | 1/2 “ | 1/2 “ | 1/2 “ |
| 40 amp | #10 | 1/2 “ | 1/2 “ | 1/2 “ |
| 50 amp | #8 | 3/4 “ | 3/4 “ | 3/4 “ |
| 60 amp | #6 | 3/4 “ | 3/4 “ | 3/4 “ |
| 70 amp | #6 | 3/4 “ | 3/4 “ | 3/4 “ |

*Based on 4 wires in the conduit (2-current carrying conductors, 1-grounded conductor, 1-equipment ground).

Identify location of electric vehicle charging station and utility panel in diagram on next page:

CHECKLIST FOR COMMERCIAL ELECTRICAL VEHICLE CHARGING STATIONS

All forms available at <website>

- Completed Building Permit Application

- X copies of site plan

- X copies of electrical plan

- Equipment Manufacturer’s Installation Instructions

For Electronic Submittals:

- PDF files of forms and plans listed

- Email all PDF files to <email>

REQUIREMENTS:

Site Plan:

( Building footprints and landscaped areas

( Parking and circulation areas

( Show locations of any existing and all proposed EV stations, panels, and other service equipment

Electrical Plan:

( Electrical and equipment layout

( Single line diagram

( Electrical Load Calculations (Existing + New) and Panel schedule

(  All plans must demonstrate compliance with accessibility provisions (see below)

| Total Number Of EVCS At Facility | Minimum Number (by type) Of EVCS Required |
| --- | --- |
|  | Van Accessible | Standard Accessible | Ambulatory |
| 1-4 | 1 | 0 | 0 |
| 5-25 | 1 | 1 | 0 |
| 26-50 | 1 | 1 | 1 |
| >50 | See CBC Table 11B-228.3.2.1 |